## Slide 1: 23-09

## Slide 2: Last week
I found the model could be improved
  MAE: 7,54ºC
  Bias: -7.16ºC
  Nominal load assumed PF = 1
  R assumed copper losses = all losses -> s = 0

## Slide 3: Adding PF and s
Adding PF and s into the model and computing least square errors to find the optimal values found:
  PF = 0.85
  s = -1.4
A negative value for s makes no physical sense
Thus, I concluded the factory parameters have drifted over time

## Slide 4: Fitting the whole model
I assumed that I would have to fit all variables to the data.
First I tried fitting one variable at a time to find the most relevant variables
They turned out to be:
(metric is MAE)

## Slide 5: Approaches for fitting the model
Fitting top 4
Fitting all
Correcting Bias (+7.16)

## Slide 6: Issues with the data
Sometimes ambient T is missing (=0.0)
(lost the picture)

## Slide 7
Outliers

## Slide 8
Model limitations (energized transformer assumption)